## UK
Note: Do not change the column/rows index
Description | UK Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story |  |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC602S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC718D | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.319 | 24V Rail(A) | NA | 40V Rail(A) | 0.498 | Total System Load(A) | 0.276 | Standby Current(A) | 0.426 | Alarm Current(A) | 8.6 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC240-2 | Node1 |  | FC | 1.082 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.572 | Total System Load(A) | 0.223 | Standby Current(A) | 0.412 | Alarm Current(A) | 7 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Belgium
Note: Do not change the column/rows index
Description | Belgium Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3445/T1714/T1718 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC604S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC708D | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.363 | 24V Rail(A) | NA | 40V Rail(A) | 0.542 | Total System Load(A) | 0.276 | Standby Current(A) | 0.476 | Alarm Current(A) | 8.64 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC702S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.319 | 24V Rail(A) | NA | 40V Rail(A) | 0.498 | Total System Load(A) | 0.276 | Standby Current(A) | 0.426 | Alarm Current(A) | 8.6 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Denmark
Note: Do not change the column/rows index
Description | Denmark Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story |  |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC604S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Norway
Note: Do not change the column/rows index
Description | Norway Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3464/T3756 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC604S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Sweden
Note: Do not change the column/rows index
Description | Sweden Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3465/T3759 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC602S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Italy
Note: Do not change the column/rows index
Description | Italy Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3443/T1983/T1985 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC602S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC32-1 | Node1 |  | FC | 1.082 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.105 | 40V Rail(A) | 0.487 | Total System Load(A) | 0.198 | Standby Current(A) | 0.388 | Alarm Current(A) | 6.23 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC240-4 | Node1 |  | FC | 1.172 | 5V Rail(A) | 0.165 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.902 | Total System Load(A) | 0.337 | Standby Current(A) | 0.527 | Alarm Current(A) | 10.51 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Spain
Note: Do not change the column/rows index
Description | Spain Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3442/T1710/T1712 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC602S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC32-1 | Node1 |  | FC | 1.082 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.105 | 40V Rail(A) | 0.487 | Total System Load(A) | 0.198 | Standby Current(A) | 0.388 | Alarm Current(A) | 6.23 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC240-2 | Node1 |  | FC | 1.082 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.572 | Total System Load(A) | 0.223 | Standby Current(A) | 0.412 | Alarm Current(A) | 7 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Romania
Note: Do not change the column/rows index
Description | Romania Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-4307/T3609/T3610 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC708D | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.363 | 24V Rail(A) | NA | 40V Rail(A) | 0.542 | Total System Load(A) | 0.276 | Standby Current(A) | 0.476 | Alarm Current(A) | 8.64 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC702S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.319 | 24V Rail(A) | NA | 40V Rail(A) | 0.498 | Total System Load(A) | 0.276 | Standby Current(A) | 0.426 | Alarm Current(A) | 8.6 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Slovakia
Note: Do not change the column/rows index
Description | Slovakia Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-4306/T3585/T3587 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC708D | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.363 | 24V Rail(A) | NA | 40V Rail(A) | 0.542 | Total System Load(A) | 0.276 | Standby Current(A) | 0.476 | Alarm Current(A) | 8.64 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC702S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.319 | 24V Rail(A) | NA | 40V Rail(A) | 0.498 | Total System Load(A) | 0.276 | Standby Current(A) | 0.426 | Alarm Current(A) | 8.6 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Hungary
Note: Do not change the column/rows index
Description | Hungary Market |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-4308/T3665/T3666 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
FC708D | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.363 | 24V Rail(A) | NA | 40V Rail(A) | 0.542 | Total System Load(A) | 0.276 | Standby Current(A) | 0.476 | Alarm Current(A) | 8.64 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC702S | Node1 |  | FC | 0.000 | 5V Rail(A) | 0.319 | 24V Rail(A) | NA | 40V Rail(A) | 0.498 | Total System Load(A) | 0.276 | Standby Current(A) | 0.426 | Alarm Current(A) | 8.6 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
FC240-4 | Node1 |  | FC | 1.172 | 5V Rail(A) | 0.165 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.902 | Total System Load(A) | 0.337 | Standby Current(A) | 0.527 | Alarm Current(A) | 10.51 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A