## Add Devices Loop A
Note: Do not change the column/rows index |  |  |  |  | DC Units on UI after adding device and Base | 364.1 |  | DC Unit Loading Details Name
Description | To verify trip current DC calculation value by adding devices and delete devices | Color Codes | [5 empty] | Current (DC Units)
Used for methods/functions | verifyTripCurrentForDCCalculation |  | Constants |  | Panel LED | 5 |  | Current (worst case)
User Story | NGC-1397 or NGC-595/TC-226 |  | Input Value |  | Max Loop Driver Load | 220
Expected value
Device | Gallery Type | Label | Default Flash rate | Default volume | Change Flash rate | Change Volume | Device DC Units | Assign Base/Default Base | Base Property Index | Base DC Units | Integral LED | Remote LED | Trip Current
801 CH | Detectors | 801 CH - 1 | NA | NA | NA | NA | 1 | 5BI 5" [517.050.018] & 801RIL | 13 | 0.3 | 1 | 0 | 7
850 PH | Detectors | 850 PH - 2 | NA | NA | NA | NA | 1.3 | 5BI 5" [517.050.018] & 801RIL | 13 | 0.3 | 1 | 0 | 10
MCP 820 | Call points | MCP 820 - 3 | NA | NA | NA | NA | 1.2 | NA | NA | NA | 1 | NA | 10

## Other Devices Loop A
Note: Do not change the column/rows index |  |  |  |  | DC Units on UI after adding other devices | 411 |  | DC Unit Loading Details Name
Description | To verify trip current DC calculation value by adding devices and delete devices | Color Codes |  |  | DC Units on UI after deleting other devices | 364.1 |  | Current (DC Units)
Used for methods/functions | verifyTripCurrentForDCCalculation |  | Constants |  | Panel LED | 5 |  | Current (worst case)
User Story | NGC-1397 or NGC-595/TC-226 |  | Input Value |  | Max Loop Driver Load | 220
Expected value
Device | Gallery Type | Label | Default Flash rate | Default volume | Change Flash rate | Change Volume | Device DC Units | Assign Base/Default Base | Base Property Index | Base DC Units | Integral LED | Remote LED | Trip Current
LPAV 3000 | Sounders/Beacons | LPAV 3000 - 4 | NA | NA | NA | NA | 33 | NA | 13 | 0 | 1 | 0 | 6
850 PH | Detectors | 850 PH - 6 | NA | NA | NA | NA | 1.3 | NA | 13 | 0 | 1 | 0 | 10
LI800 | Other | LI800 | NA | NA | NA | NA | 0.6 | NA | NA | NA | 1 | NA | 2.5