## Germany
Note: Do not change the column/rows index
Description |  |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3475/T1839 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
P805D | Node1 |  | P | 0.329 | 5V Rail(A) | 0.291 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.629 | Total System Load(A) | 0.410 | Standby Current(A) | 0.564 | Alarm Current(A) | 12.72 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
Pro215S Lite | Node1 |  | MT | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
MZX254 | Node1 |  |  | 1.070 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.569 | Total System Load(A) | 0.223 | Standby Current(A) | 0.410 | Alarm Current(A) | 7 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Belgium
Note: Do not change the column/rows index
Description |  |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3478/T2321 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
P805D | Node1 |  | P | 0.329 | 5V Rail(A) | 0.291 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.629 | Total System Load(A) | 0.410 | Standby Current(A) | 0.564 | Alarm Current(A) | 12.72 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
Pro415D Lite | Node1 |  | MT | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
MZX125 | Node1 |  |  | 1.062 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.105 | 40V Rail(A) | 0.483 | Total System Load(A) | 0.198 | Standby Current(A) | 0.383 | Alarm Current(A) | 6.23 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A

## Czech
Note: Do not change the column/rows index
Description |  |  | Color Codes
Used for methods/functions |  |  |  | Constants
User Story | NGC-3477/T1869 |  |  | Input Value
Expected value
Panel Name | PanelNode | CPUType | PanelType | expectedDefault5V | LoadingDetailName5V | expectedDefault24V | LoadingDetailName24V | expectedDefault40V | LoadingDetailName40V | expectedDefaultTotalSystemLoad | LoadingDetailNameTotalSystemLoad | expectedDefaultStandby Current | LoadingDetailNameStandby Current | expectedDefaultAlarm Current | LoadingDetailNameAlarm Current | expectedDefaultBatterySize | LoadingDetailNameMinimumBatterySize | expectedDefault AC Units | expectedDefault DC Units | expectedDefault Volt Drop Mean | expectedDefault Volt Drop Worst | Loading Loop Name
P805D | Node1 |  | P | 0.329 | 5V Rail(A) | 0.291 | 24V Rail(A) | 0.160 | 40V Rail(A) | 0.629 | Total System Load(A) | 0.410 | Standby Current(A) | 0.564 | Alarm Current(A) | 12.72 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
Pro415S Lite | Node1 |  | MT | 0.000 | 5V Rail(A) | 0.220 | 24V Rail(A) | NA | 40V Rail(A) | 0.399 | Total System Load(A) | 0.220 | Standby Current(A) | 0.314 | Alarm Current(A) | 6.84 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A
ZX1 | Node1 |  |  | 1.211 | 5V Rail(A) | 0.100 | 24V Rail(A) | 0.105 | 40V Rail(A) | 0.555 | Total System Load(A) | 0.250 | Standby Current(A) | 0.562 | Alarm Current(A) | 7.92 | Minimum Battery size(Ah) | 0 | 220 | 0.00 | 0.00 | Built-in Loop-A